## simulation
Start Date | Length (weeks) | Cost of CFM ($)
start | length | cost_cfm
"2014-01-01" | 26 | 5.25

## laboratories
Basic Info |  |  |  | Ventilation Information | [9 empty] | Behavioral Information | [7 empty] | Other
Lab Name | Area (sqft) | Ceiling (ft) | Hood List | Day Occ. ACH | Day Unoc. ACH | Night Occ. ACH | Night UnOcc. ACH | Day ACH Start Time | Night ACH Start Time | Net Lab Flow (cfm) | Add. Equip. Min (cfm) | Add. Equip. Max (cfm) | Occupancy Detection | Day Occ. Probability | Night Occ. Probability | Day Occ. Start | Night Occ. Start | WkEnd Day Occ. Start | WkEnd Night Occ. Start | WkEnd Day Occ. Prob. | WkEnd Night Occ. Prob. | Notes
lab_id | surface_area | ceil_height | hoods | day_occupied_ach | day_unoccupied_ach | night_occupied_ach | night_unoccupied_ach | ach_day_start | ach_night_start | additional_evac | additional_equipment_min | additional_equipment_max | occupancy_detection_type | day_occupancy_rate | night_occupancy_rate | day_occupancy_start | night_occupancy_start | weekend_day_occupancy_start | weekend_night_occupancy_start | weekend_day_occupancy_rate | weekend_night_occupancy_rate | notes
Bellini-156 | 1330.6333 | 8 |  | 7.4524 | 3.7262 | 7.4524 | 3.7262 | 8:00 | 20:00 | 0 | 0 | 0 |  | 0.9 | 0.2 | 8:00 | 20:00 | 8:00 | 20:00 | 0.7 | 0.1
Bellini-157 | 1305.7687 | 8 |  | 7.5943 | 3.7972 | 7.5943 | 3.7972 | 8:00 | 20:00 | 0 | 0 | 0 |  | 0.9 | 0.2 | 8:00 | 20:00 | 8:00 | 20:00 | 0.7 | 0.1
Bellini-170 | 1320.7305 | 8 |  | 7.2436 | 3.6218 | 7.2436 | 3.6218 | 8:00 | 20:00 | 0 | 0 | 0 |  | 0.9 | 0.2 | 8:00 | 20:00 | 8:00 | 20:00 | 0.7 | 0.1
Bellini-173 | 1312.9805 | 8 |  | 7.6252 | 3.8126 | 7.6252 | 3.8126 | 8:00 | 20:00 | 0 | 0 | 0 |  | 0.9 | 0.2 | 8:00 | 20:00 | 8:00 | 20:00 | 0.7 | 0.1
Bellini-256 | 1325.6819 | 8 |  | 6.4493 | 3.2247 | 6.4493 | 3.2247 | 8:00 | 20:00 | 0 | 0 | 0 |  | 0.9 | 0.2 | 8:00 | 20:00 | 8:00 | 20:00 | 0.7 | 0.1
Bellini-257 | 1306.6298 | 8 |  | 6.5434 | 3.2717 | 6.5434 | 3.2717 | 8:00 | 20:00 | 0 | 0 | 0 |  | 0.9 | 0.2 | 8:00 | 20:00 | 8:00 | 20:00 | 0.7 | 0.1
Bellini-270 | 1315.1333 | 8 |  | 6.5011 | 3.2505 | 6.5011 | 3.2505 | 8:00 | 20:00 | 0 | 0 | 0 |  | 0.9 | 0.2 | 8:00 | 20:00 | 8:00 | 20:00 | 0.7 | 0.1
Bellini-273 | 1312.6576 | 8 |  | 6.5133 | 3.2567 | 6.5133 | 3.2567 | 8:00 | 20:00 | 0 | 0 | 0 |  | 0.9 | 0.2 | 8:00 | 20:00 | 8:00 | 20:00 | 0.7 | 0.1
Bellini-356 | 1330.2028 | 8 |  | 8.0761 | 4.038 | 8.0761 | 4.038 | 8:00 | 20:00 | 0 | 0 | 0 |  | 0.9 | 0.2 | 8:00 | 20:00 | 8:00 | 20:00 | 0.7 | 0.1
Bellini-356A | 122.3855 | 8 |  | 28.4371 | 14.1536 | 28.4371 | 14.1536 | 8:00 | 20:00 | 0 | 0 | 0 |  | 0.9 | 0.2 | 8:00 | 20:00 | 8:00 | 20:00 | 0.7 | 0.1
Bellini-357 | 1305.7687 | 8 |  | 6.5477 | 3.2738 | 6.5477 | 3.2738 | 8:00 | 20:00 | 0 | 0 | 0 |  | 0.9 | 0.2 | 8:00 | 20:00 | 8:00 | 20:00 | 0.7 | 0.1
Bellini-370 | 1315.1333 | 8 |  | 6.5011 | 3.2505 | 6.5011 | 3.2505 | 8:00 | 20:00 | 0 | 0 | 0 |  | 0.9 | 0.2 | 8:00 | 20:00 | 8:00 | 20:00 | 0.7 | 0.1
Bellini-373 | 1312.7652 | 8 |  | 6.5128 | 3.2564 | 6.5128 | 3.2564 | 8:00 | 20:00 | 0 | 0 | 0 |  | 0.9 | 0.2 | 8:00 | 20:00 | 8:00 | 20:00 | 0.7 | 0.1
Bellini-456 | 1330.2028 | 8 |  | 8.2911 | 4.1456 | 8.2911 | 4.1456 | 8:00 | 20:00 | 0 | 0 | 0 |  | 0.9 | 0.2 | 8:00 | 20:00 | 8:00 | 20:00 | 0.7 | 0.1
Bellini-457 | 1305.7687 | 8 |  | 7.9108 | 3.9554 | 7.9108 | 3.9554 | 8:00 | 20:00 | 0 | 0 | 0 |  | 0.9 | 0.2 | 8:00 | 20:00 | 8:00 | 20:00 | 0.7 | 0.1
Bellini-470 | 1315.1333 | 8 |  | 7.7819 | 3.891 | 7.7819 | 3.891 | 8:00 | 20:00 | 0 | 0 | 0 |  | 0.9 | 0.2 | 8:00 | 20:00 | 8:00 | 20:00 | 0.7 | 0.1
Bellini-473 | 1312.6576 | 8 |  | 7.5666 | 3.7833 | 7.5666 | 3.7833 | 8:00 | 20:00 | 0 | 0 | 0 |  | 0.9 | 0.2 | 8:00 | 20:00 | 8:00 | 20:00 | 0.7 | 0.1
Core-344 | 433.1393 | 8 |  | 12.4745 | 6.2372 | 12.4745 | 6.2372 | 8:00 | 20:00 | 0 | 0 | 0 |  | 0.9 | 0.2 | 8:00 | 20:00 | 8:00 | 20:00 | 0.7 | 0.1
Core-345 | 338.0941 | 8 |  | 6.4395 | 3.1963 | 6.4395 | 3.1963 | 8:00 | 20:00 | 0 | 0 | 0 |  | 0.9 | 0.2 | 8:00 | 20:00 | 8:00 | 20:00 | 0.7 | 0.1
Core-452 | 548.4207 | 8 |  | 10.9534 | 5.4767 | 10.9534 | 5.4767 | 8:00 | 20:00 | 0 | 0 | 0 |  | 0.9 | 0.2 | 8:00 | 20:00 | 8:00 | 20:00 | 0.7 | 0.1
Core-446 | 359.6219 | 8 |  | 7.1146 | 3.5794 | 7.1146 | 3.5794 | 8:00 | 20:00 | 0 | 0 | 0 |  | 0.9 | 0.2 | 8:00 | 20:00 | 8:00 | 20:00 | 0.7 | 0.1
Cancer-3350 | 600 | 8 |  | 9.2702 | 4.6351 | 9.2702 | 4.6351 | 8:00 | 20:00 | 0 | 0 | 0 |  | 0.9 | 0.2 | 8:00 | 20:00 | 8:00 | 20:00 | 0.7 | 0.1 | Unsure of square footage
Cancer-401A | 500.4137 | 8 |  | 5.5258 | 0 | 5.5258 | 0 | 8:00 | 20:00 | 0 | 0 | 0 |  | 0.9 | 0.2 | 8:00 | 20:00 | 8:00 | 20:00 | 0.7 | 0.1
Cancer-401 | 613.5423 | 8 |  | 2.901 | 0 | 2.901 | 0 | 8:00 | 20:00 | 0 | 0 | 0 |  | 0.9 | 0.2 | 8:00 | 20:00 | 8:00 | 20:00 | 0.7 | 0.1
Cancer-403B | 1735.356 | 8 |  | 6.914 | 3.4616 | 6.914 | 3.4616 | 8:00 | 20:00 | 0 | 0 | 0 |  | 0.9 | 0.2 | 8:00 | 20:00 | 8:00 | 20:00 | 0.7 | 0.1
Cancer-403G | 111.4064 | 8 |  | 92.1498 | 46.0749 | 92.1498 | 46.0749 | 8:00 | 20:00 | 0 | 0 | 0 |  | 0.9 | 0.2 | 8:00 | 20:00 | 8:00 | 20:00 | 0.7 | 0.1
Cancer-411B | 1902.627 | 8 |  | 8.6783 | 4.335 | 8.6783 | 4.335 | 8:00 | 20:00 | 0 | 0 | 0 |  | 0.9 | 0.2 | 8:00 | 20:00 | 8:00 | 20:00 | 0.7 | 0.1
Cancer-503B | 1679.9219 | 8 |  | 6.0827 | 3.0366 | 6.0827 | 3.0366 | 8:00 | 20:00 | 0 | 0 | 0 |  | 0.9 | 0.2 | 8:00 | 20:00 | 8:00 | 20:00 | 0.7 | 0.1
Cancer-503G | 79.3299 | 8 |  | 30.4494 | 15.2247 | 30.4494 | 15.2247 | 8:00 | 20:00 | 0 | 0 | 0 |  | 0.9 | 0.2 | 8:00 | 20:00 | 8:00 | 20:00 | 0.7 | 0.1
Cancer-511B | 1901.9811 | 8 |  | 6.208 | 3.1082 | 6.208 | 3.1082 | 8:00 | 20:00 | 0 | 0 | 0 |  | 0.9 | 0.2 | 8:00 | 20:00 | 8:00 | 20:00 | 0.7 | 0.1
Cancer-603B | 1682.1823 | 8 |  | 5.8194 | 2.9097 | 5.8194 | 2.9097 | 8:00 | 20:00 | 0 | 0 | 0 |  | 0.9 | 0.2 | 8:00 | 20:00 | 8:00 | 20:00 | 0.7 | 0.1
Cancer-603H | 115.2814 | 8 |  | 36.3929 | 18.1964 | 36.3929 | 18.1964 | 8:00 | 20:00 | 0 | 0 | 0 |  | 0.9 | 0.2 | 8:00 | 20:00 | 8:00 | 20:00 | 0.7 | 0.1
Cancer-611B | 118.08 | 8 |  | 82.9041 | 41.4521 | 82.9041 | 41.4521 | 8:00 | 20:00 | 0 | 0 | 0 |  | 0.9 | 0.2 | 8:00 | 20:00 | 8:00 | 20:00 | 0.7 | 0.1

## fumehoods
Basic Information |  |  |  | Ventilation Information |  |  |  | Behavioural Information |  | Other
Hood ID | Lab Name | Width (inches) | Height (inches) | Max Flow (cfm) | Min Flow (cfm) | Face Vel. Occ. (fpm) | Face Vel. Unoc. (fpm) | Sash Profile | Occ. Probability | Notes
hood_id | lab_id | max_sash_height | sash_width | max_cfm | min_cfm | face_vel_occupied | face_vel_unoccupied | sash_profile | hood_use_rate | notes
BH01-1620 | Bellini-156 | 29.5 | 51 | 1045 | 208 | 100 | 100 | mid | 0.4
BH01-1720 | Bellini-157 | 29.5 | 51 | 1045 | 208 | 100 | 100 | mid | 0.4
BH01-1830 | Bellini-170 | 29.5 | 51 | 1045 | 208 | 100 | 100 | mid | 0.4
BH01-1930 | Bellini-173 | 29.5 | 51 | 1045 | 208 | 100 | 100 | mid | 0.4
BH01-2620 | Bellini-256 | 29.5 | 51 | 1045 | 208 | 100 | 100 | mid | 0.4
BH02-2620 | Bellini-257 | 29.5 | 51 | 1045 | 208 | 100 | 100 | mid | 0.4
BH01-2720 | Bellini-257 | 29.5 | 51 | 1045 | 208 | 100 | 100 | mid | 0.4
BH02-2720 | Bellini-258 | 29.5 | 51 | 1045 | 208 | 100 | 100 | mid | 0.4
BH01-2830 | Bellini-270 | 29.5 | 51 | 1045 | 208 | 100 | 100 | mid | 0.4
BH02-2830 | Bellini-271 | 29.5 | 51 | 1045 | 208 | 100 | 100 | mid | 0.4
BH01-2930 | Bellini-273 | 29.5 | 51 | 1045 | 208 | 100 | 100 | mid | 0.4
BH02-2930 | Bellini-274 | 29.5 | 51 | 1045 | 208 | 100 | 100 | mid | 0.4
BH01-3360 | Cancer-3350 | 29.5 | 51 | 1045 | 208 | 100 | 100 | mid | 0.4
BH01-3515 | Core-344 | 29.5 | 51 | 1045 | 208 | 100 | 100 | mid | 0.4
BH01-3530 | Core-345 | 29.5 | 51 | 1045 | 208 | 100 | 100 | mid | 0.4
BH01-3620 | Bellini-356 | 29.5 | 51 | 1045 | 208 | 100 | 100 | mid | 0.4
BH02-3620 | Bellini-357 | 29.5 | 51 | 1045 | 208 | 100 | 100 | mid | 0.4
BH01-3630 | Bellini-356A | 29.5 | 51 | 1045 | 208 | 100 | 100 | mid | 0.4
BH01-3720 | Bellini-357 | 29.5 | 51 | 1045 | 208 | 100 | 100 | mid | 0.4
BH02-3720 | Bellini-358 | 29.5 | 51 | 1045 | 208 | 100 | 100 | mid | 0.4
BH01-3830 | Bellini-370 | 29.5 | 51 | 1045 | 208 | 100 | 100 | mid | 0.4
BH02-3830 | Bellini-371 | 29.5 | 51 | 1045 | 208 | 100 | 100 | mid | 0.4
BH01-3930 | Bellini-373 | 29.5 | 51 | 1045 | 208 | 100 | 100 | mid | 0.4
BH02-3930 | Bellini-374 | 29.5 | 51 | 1045 | 208 | 100 | 100 | mid | 0.4
BH01-4010 | Cancer-401A | 29.5 | 51 | 1045 | 208 | 100 | 100 | mid | 0.4
BH01-4030 | Cancer-401 | 29.5 | 51 | 1045 | 208 | 100 | 100 | mid | 0.4
BH01-4130 | Cancer-403B | 29.5 | 51 | 1045 | 208 | 100 | 100 | mid | 0.4
BH02-4130 | Cancer-403B | 29.5 | 51 | 1045 | 208 | 100 | 100 | mid | 0.4
BH03-4130 | Cancer-403B | 29.5 | 51 | 1045 | 208 | 100 | 100 | mid | 0.4
BH01-4135 | Cancer-403G | 29.5 | 51 | 1045 | 208 | 100 | 100 | mid | 0.4
BH01-4310 | Cancer-411B | 29.5 | 51 | 1045 | 208 | 100 | 100 | mid | 0.4
BH02-4310 | Cancer-411B | 29.5 | 51 | 1045 | 208 | 100 | 100 | mid | 0.4
BH03-4310 | Cancer-411B | 29.5 | 51 | 1045 | 208 | 100 | 100 | mid | 0.4
BH01-4535 | Core-446 | 29.5 | 51 | 1045 | 208 | 100 | 100 | mid | 0.4
BH01-4572 | Core-452 | 29.5 | 63 | 1290 | 240 | 100 | 100 | mid | 0.4
BH02-4572 | Core-453 | 29.5 | 63 | 1290 | 240 | 100 | 100 | mid | 0.4
BH03-4572 | Core-454 | 29.5 | 63 | 1290 | 240 | 100 | 100 | mid | 0.4
BH04-4572 | Core-455 | 29.5 | 63 | 1290 | 240 | 100 | 100 | mid | 0.4
BH01-4620 | Bellini-456 | 29.5 | 51 | 1045 | 208 | 100 | 100 | mid | 0.4
BH02-4620 | Bellini-457 | 29.5 | 51 | 1045 | 208 | 100 | 100 | mid | 0.4
BH03-4620 | Bellini-458 | 29.5 | 51 | 1045 | 208 | 100 | 100 | mid | 0.4
BH01-4720 | Bellini-457 | 29.5 | 51 | 1045 | 208 | 100 | 100 | mid | 0.4
BH02-4720 | Bellini-458 | 29.5 | 51 | 1045 | 208 | 100 | 100 | mid | 0.4
BH03-4720 | Bellini-459 | 29.5 | 51 | 1045 | 208 | 100 | 100 | mid | 0.4
BH01-4830 | Bellini-470 | 29.5 | 51 | 1045 | 208 | 100 | 100 | mid | 0.4
BH02-4830 | Bellini-471 | 29.5 | 51 | 1045 | 208 | 100 | 100 | mid | 0.4
BH03-4830 | Bellini-472 | 29.5 | 51 | 1045 | 208 | 100 | 100 | mid | 0.4
BH01-4930 | Bellini-473 | 29.5 | 51 | 1045 | 208 | 100 | 100 | mid | 0.4
BH02-4930 | Bellini-474 | 29.5 | 51 | 1045 | 208 | 100 | 100 | mid | 0.4
BH03-4930 | Bellini-475 | 29.5 | 51 | 1045 | 208 | 100 | 100 | mid | 0.4
BH01-5130 | Cancer-503B | 29.5 | 51 | 1045 | 208 | 100 | 100 | mid | 0.4
BH02-5130 | Cancer-503B | 29.5 | 51 | 1045 | 208 | 100 | 100 | mid | 0.4
BH03-5130 | Cancer-503B | 29.5 | 51 | 1045 | 208 | 100 | 100 | mid | 0.4
BH01-5135 | Cancer-503G | 29.5 | 51 | 1045 | 208 | 100 | 100 | mid | 0.4
BH01-5310 | Cancer-511B | 29.5 | 51 | 1045 | 208 | 100 | 100 | mid | 0.4
BH02-5310 | Cancer-511B | 29.5 | 51 | 1045 | 208 | 100 | 100 | mid | 0.4
BH03-5310 | Cancer-511B | 29.5 | 51 | 1045 | 208 | 100 | 100 | mid | 0.4
BH01-6130 | Cancer-603B | 29.5 | 51 | 1045 | 208 | 100 | 100 | mid | 0.4
BH02-6130 | Cancer-603B | 29.5 | 51 | 1045 | 208 | 100 | 100 | mid | 0.4
BH03-6130 | Cancer-603B | 29.5 | 51 | 1045 | 208 | 100 | 100 | mid | 0.4
BH01-6135 | Cancer-603H | 29.5 | 51 | 1045 | 208 | 100 | 100 | mid | 0.4
BH01-6310 | Cancer-611B | 29.5 | 51 | 1045 | 208 | 100 | 100 | mid | 0.4
BH02-6310 | Cancer-611B | 29.5 | 51 | 1045 | 208 | 100 | 100 | mid | 0.4
BH03-6310 | Cancer-611B | 29.5 | 51 | 1045 | 208 | 100 | 100 | mid | 0.4
Note on I2: Marc: Can be: A - chosen from ["very_low", "low", "mid", "high", "very_high"] B - an integer (NO decimal point) e.g. "70", which specifies a constant sash height at that level. C - a file name e.g. "bac_1234.csv"

## scenarios
Scenario Name | Description | Sash Profile | Face Vel. Unoc. (fpm)
name | description | sash_profile | face_vel_unoccupied
current_op | current operation | as_is | as_is
reduced_face | reduced face vel 40% | as_is | replace_all:60
sash_high | sash reduced 20% | replace_all:high | as_is
sash_low | sash reduced 50% | replace_all:low | as_is
sash_very_low | reduced face vel 40%, sash reduced 20% | replace_all:very_low | as_is
best case usage | best case usage | replace_all:0 | as_is
worst case usage | worst case usage | replace_all:100 | as_is